| A | PHOTOGRAPH #: 1 DESCRIPTION: Front of building Street entrance from highway 17 for public. Main access entry through front door; residential urban neighbourhood area |  |
| --- | --- | --- |
| B | PHOTOGRAPH # 2 DESCRIPTION: Street view Main commercial building with subsidiary structure and residential homes in close proximity. |  |
| C | PHOTOGRAPH #: 3 DESCRIPTION: Picture taken at the front facing the building. Building and existing deck with roof structure of combustible construction materials. |  |
| D | PHOTOGRAPH #: 4 DESCRIPTION: Interior of building. Interior commercial cooking equipment present consisting of deep fryers and adjacent grill; connected to and supplied by natural gas system. |  |
| E | PHOTOGRAPH #: 5 DESCRIPTION: Interior of building, Exhaust and ventilation hood system above commercial cooking equipment. Exhaust and ventilation hood with lack of fire protection system; open seams,hazardous activities |  |
| F | PHOTOGRAPH #: 6 DESCRIPTION: Hood filters above commercial cooking equipment. Accumulations of combustible deposits present; lack of proper maintenance, routine cleaning. |  |
| G | PHOTOGRAPH #: 7 DESCRIPTION: Hood filters above commercial cooking equipment Seams, joints and penetrations not sealed; combustible deposits (from grease laden vapours) not captured in exhaust and ventilation system. |  |
| H | PHOTOGRAPH #: 8 DESCRIPTION: Hood filters above commercial cooking equipment with light fixture located adjacent to hood and above commercial cooking equipment. Hazardous activities; unapproved use. |  |
| I | PHOTOGRAPH #: 9 DESCRIPTION: Hood filters above commercial cooking equipment; fan located below passing through to exterior of building. Accumulation of combustible deposits on walls, fan and cables; hazardous activities. |  |
| J | PHOTOGRAPH #: 10 DESCRIPTION: Fan located under and adjacent to hood and passing through to exterior of building. Accumulation of combustible deposits on fan blades and housing; hazardous activities. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| K | PHOTOGRAPH #: 11 DESCRIPTION: Exterior of building. Fan vents passing through to exterior of building. Accumulation of combustible deposits on walls, vents, exterior surfaces if building; fixed in combustible materials (OSB boards), hazardous activities. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| L | PHOTOGRAPH #: 12 DESCRIPTION: Picture taken of Exterior Ventilation/exhaust system located on roof of building. Accumulations of combustible deposits on exterior surface of roof of building; hazardous activities. |  |
| M | PHOTOGRAPH #: 13 DESCRIPTION: : Picture taken of Exterior Ventilation/exhaust system located on roof of building. Accumulations of combustible deposits on exterior surface of roof of building; ventilation equipment and supporting members; hazardous activities. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| N | PHOTOGRAPH #: 14 DESCRIPTION: Interior window; covered with mesh screen. Accumulations of combustible deposits on screen, hazardous activities. |  |
| O | PHOTOGRAPH #: 15 DESCRIPTION: Picture taken from outside of building for the Interior window; covered with mesh screen. Accumulations of combustible deposits on screen, hazardous activities. Contributes to hazardous activities; |  |
| P | PHOTOGRAPH #: 16 DESCRIPTION: Exterior of building, rear side, exterior cladding consisting of OSB. Exposed foam insulation, improper installation, exterior walls seams open. |  |
| Q | PHOTOGRAPH #: 17 DESCRIPTION: Exterior of building, rear side, exterior cladding consisting of OSB. Natural Gas connection. Concrete block foundation showing. |  |
| R | PHOTOGRAPH #: 18 DESCRIPTION: Exterior of building, rear side. Natural Gas meter adjacent to building. |  |
| S | PHOTOGRAPH #: 19 DESCRIPTION: Interior of building; existing electrical panel. Not secured against unauthorized access, no visible indicators of licensed installation and no records present, storage of combustible materials; hazardous activities. |  |
| T | PHOTOGRAPH #: 20 DESCRIPTION: Interior of building. Electrical installation in close proximity to water use (sinks) and not in conformance with Electrical Safety Act; hazardous. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| U | PHOTOGRAPH #: 21 DESCRIPTION: Interior of building. Exposed wood support beam and electrical wiring breaching fire separation. Construction of building extended from original mobile trailer unit. Change if use. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| V | PHOTOGRAPH #: 22 DESCRIPTION: interior of building; compressor above fridge. Exposed compressor above fridge, presence of accumulation of combustible deposits due to lack of proper ventilation system installation and maintenance; hazardous activities. |  |
| W | PHOTOGRAPH #: 23 DESCRIPTION: Interior of building Demonstrating different combustible materials used in construction of building which forms part of a mobile trailer unit. |  |
| X | PHOTOGRAPH #: 24 DESCRIPTION: Interior of building. Exposed wood support beam and electrical wiring breaching fire separation. Construction of building extended from original mobile trailer unit. Change if use. |  |
| Y | PHOTOGRAPH #: 25 DESCRIPTION: Interior of building; Electrical service outlet installation without a cover in conformance with Electrical Safety Code. Contributes to hazardous activities; danger to occupants in the case of fire. |  |
| Z | PHOTOGRAPH # 26 DESCRIPTION: Interior of building. Single fire extinguisher; not maintained in accordance with NFPA 10, last maintenance date not indicated or present, no maintenance or inspection records available. Not sufficient to address a grease fire. |  |
| A1 | PHOTOGRAPH #27 DESCRIPTION: interior of building. Exposed wood support beam and electrical wiring breaching fire separation. Construction of building extended from original mobile trailer unit. Change if use; hazardous activities. |  |