Semi-Annual / Annual

INSPECTION AND MAINTENANCE RECORD

EMERGENCY GENERATOR

See Reverse for Required Procedure

Semi Annual

Date:__________________                                             Performed by:_____________________________

| Maintenance Work Performed | Corrective Work Performed | Parts Replaced |
| --- | --- | --- |

Is Unit Ready for Start Up?:__________________           Signature: _______________________________

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Annual

Date:__________________                                              Performed by:_____________________________

| Maintenance Work Performed | Corrective Work Performed | Parts Replaced |
| --- | --- | --- |

Is Unit Ready for Start Up?:__________________           Signature: _______________________________

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Semi Annual

Date___________________                                              Performed by:_____________________________

| Maintenance Work Performed | Corrective Work Performed | Parts Replaced |
| --- | --- | --- |

Is Unit Ready for Start Up?:__________________           Signature: _______________________________

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Annual

Date___________________                                              Performed by:_____________________________

| Maintenance Work Performed | Corrective Work Performed | Parts Replaced |
| --- | --- | --- |

Is Unit Ready for Start Up?:__________________           Signature: _______________________________

EMERGENCY GENERATOR – INSPECTION PROCEDURE

EVERY SIX MONTHS	ENGINE

- Check/clean crankcase breathers, lubricate governor and linkages.

ANNUALLY			PANEL

- 1) Check electrical connections at main circuit breaker switch and breaker operation; clean insulators and bushings; check voltage regulator operation.

- 2) Isolate the panel – open all inspection covers- tighten all electrical connections.  Inspect breaker and disconnect contacts.  Clean and dress as necessary.  Operate all moving parts to ensure they move freely.  Remove all dust.  Check gauge calibration.  Clean and lubricate linkages.

TRANSFER SWITCH

- Carry out same procedures as described in item 2 – PANEL

ENGINE

- Change lube oil and filters.  Check strength of antifreeze (if applicable). Change fuel oil filters.  Change governor oil (if applicable).  Inspect and clean exhaust system.  Change gasoline (if applicable).

GENERATOR

- Test surge suppressor and rotating rectifier on brushless machines.  Grease bearings (replace old grease with new).  Re-seat brushes.  Clean commutator and slip rings.  Clean rotor and stator windings (compressed air).  Check coupling bolts and alignment.  Check conduit tightness.  Inspect windings at rotor and stator slots.  Tighten all electrical connections.

EVERY TWO YEARS	GENERATOR/ENGINE

- Check torque head bolts and re-check valve settings.

- Open access covers and check all bolts, nuts, split ring for security.

EVERY THREE YEARS	ENGINE

- Check valve settings (3 years or 500 hours, whichever is first).

- Clean and service injector nozzles (3 years of 500 hours, whichever is first).

EVERY FIVE YEARS	GENERATOR

- Check insulation of generator windings.  Use insulation tester (megger).  Valve should be not les than resistance in megohms = rated volts + 1000

If less, dry out by auxiliary heat process 	                           1000