QUARTERLY TEST RECORD

FIREFIGHTERS ELEVATORS

See Reverse for Required Procedure

|  | QUARTERLY TEST |  |
| --- | --- | --- |
| LOCATION OR I.D. NO. OF ELEVATOR | DATE OF TEST | SIGNATURE | REMARKS Description of Problems Noted and Corrective Action Taken |

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________

_____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________ _____________________________________________________

ATTACH ADDITIONAL SHEETS IF FURTHER REMARKS ARE REQUIRED

FIREFIGHTERS ELEVATORS

Reference Ontario Fire Code, subsection 7.2.2

EVERY	a)	Test elevator door opening devices that are operated by means of photo-electric

THREE		cells to ensure that the device becomes inoperative after the door has been held

MONTHS		open for more than 10 seconds with the photo-electric cell covered.

b) Test key operated switches located outside the elevator shaft to ensure that actuation

of the switch will render the “emergency stop” switch in each car inoperative and

bring all cars to the street floor or transfer lobby by cancelling all other calls after

the car has stopped at the next floor at which it can make a normal stop.

c)	 Test key operated switches in each elevator car to ensure that the actuation of the

switch will:

i)	 enable the elevator to operate independently of other elevators.

ii)  allow operation of the elevator without interference from floor call buttons.

iii)  render door protective devices inoperative.

iv)  control the opening of power-operated doors only by continuous pressure on the

door opening buttons or switches.

v) 	ensure that if the “Door Open” button is released while the door is opening, the doors

will automatically close.

AS		Ensure elevator control keys are available in a suitably identified box near the elevators

REQUIRED	 	and at the central alarm and control facility.

ensure the fire fighters’ elevator identification decal is maintained in an acceptable 			condition.