ANNUAL INSPECTION & TEST RECORD

SPRINKLER SYSTEM

See Reverse for Required Procedure

| SYSTEM LOCATION OR I.D. NO. |  | (WET ( DRY |
| --- | --- | --- |
| REMARKS Use one sheet per system. |
| DATE OF TEST |  |
| SIGNATURE |  |

SPRINKLER SYSTEMS

Reference Ontario Fire Code section 6.5 and N.F.P.A. 13

ANNUALLY	Check all sprinkler heads for damage, corrosion, grease, dust and paint.  Replace heads where necessary.

Ensure all exposed sprinkler pipe hangers are in good condition.

Remove the plugs or caps form the outside fire department connections and inspect the threads for wear, rust or obstructions.  Re-install plugs or caps wrench tight.

ANNUAL TESTS	a)  On wet sprinkler systems conduct a waterflow alarm test using the most hydraulically remote test connection.

b)  On dry sprinkler systems the dry pipe valves are to be tripped by means of the system test pipe to ensure that they operate satisfactorily and that the sprinkler alarms are in operating condition.

FOLLOWING	Test sprinkler water pressure with the main drain valve fully open to

TEST A OR B	determine that there are no obstructions or deterioration of the main water supply.

EVERY	Dry pipe systems shall be inspected for obstructions in the sprinkler

FIFTEEN	piping and if necessary, the entire system flushed of foreign material.

YEARS