WEEKLY INSPECTION & TEST RECORD

EMERGENCY GENERATOR

See Reverse for Required Procedure

| DATE | SIGNATURE | REMARKS (Attach additional sheet if required ) |
| --- | --- | --- |

EMERGENY GENERATOR

Reference Ontario Fire Code section 6.7 and C.S.A. C282-1977

SYSTEMS OPERATION TEST

WEEKLY	The emergency electrical power shall be completely tested at lest weekly as described below.

A periodic test of the system operation shall:

a) Simulate a failure of the normal supply;

b) Be arranged so that:

i) An engine generator set operates under at lest 50% of the rated load for 30 minutes, 		   and;

ii) All automatic transfer switches are operated under load;

c) Include an inspection for correct function of all auxiliary equipment such as radiator shutter 	    control, coolant pumps, fuel transfer pumps, oil coolers and engine room ventilation controls;

d) Include recording the readings of all instruments associated with the prime mover and 	  	    generator and verification they are normal; and,

e) Be carried out, logged and reported as further prescribed in the manual of instruction for 	     operation and maintenance supplied by the manufacturer.

SYSTEM INSPECTION

WEEKLY	Inspect; fuel tank level; lubricating oil level; engine coolant; heaters; lubricant and/or coolant.

Examine engine, generator, fuel tanks and cooling systems for evidence of leakage.  Check operation of fuel transfer pump if available.

ELECTRIC MOTOR SYSTEM

Examine starting system – batteries, etc., for leakage, cleanliness and terminal security.

AIR MOTOR SYSTEM

Check air tanks for pressure.  Check valves for leakage.  Check operation of auxiliary engine and compressor.  Bleed off any condensation.

BATTERIES

Check electrolyte level; specific gravity; electrical connections for tightness; check for leaks and sulphation, cleanliness and dryness between terminal posts.

ENGINE

Check governor control linkages and oil level (if applicable), fuel pump, oil sump (if applicable), fan belts and protective devices.

GENERATOR

Check brush operation for sparking and for bearing seal leakage.

PANEL

Check panel covers are secure, annunciator lamps are operational.