MONTHLY TEST RECORD

SPRINKLER SYSTEM

See reverse for Required Procedure

Use one Sheet per System

| SYSTEM LOCATION OR I..D. NO. (WET ( DRY |
| --- |
| DATE | SIGNATURE | TEST PERFORMED | REMARKS Problems Noted and Corrective Action Taken Attach additional sheets if further Remarks Required |
|  |  | MONTHLY TEST | 2 MONTH TEST | 6 MONTH TEST |  |

SPRINKLER SYSTEMS

Reference Ontario Fire Code, section 6.5 and N.F.P.A. 13

WEEKLY 	Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections are to be checked weekly to ensure that they are in the open position.

Air pressure gauges on dry pipe systems are to be checked weekly and the system maintained at the required pressure.

NOTE:  It is not necessary to record the results of the Weekly checks.

MONTHLY	Test alarm at the alarm test connection located at the sprinkler valve.

EVERY TWO	Test all transmitters and water flow actuated devices of an electrically supervised system.

MONTHS

EVERY SIX	Test all gate valve supervisory switches, building temperature sensing devices, and all other

MONTHS	sprinkler system supervisory devices of an electrically supervised system.